## Sheet1
Plug-in Electric Vehicle Load Calculator for Level 2 Charging
INSTRUCTIONS: Review the list of electrical loads in the table below and check all that exist in your home (don't forget to include the proposed Level 2 charger). For each item checked, fill in the corresponding "Watts Used" (refer to the "Typical Usage" column for wattage information). The spreadsheet should automatically populate the "TOTAL WATTS USED" column at the bottom of the table with the sum of all the numbers that are written in the "Watts Used" column. Go to the next sheet to determine if your existing electric service will accomodate the new loads
(Loads shown are rough estimates; actual loads may vary. For a more precise analysis, use the nameplate ratings for appliances and other loads and consult with a trained electrical professional.)
Check all Applicable Loads | Description of Load |  | Typical Usage | Watts Used
GENERAL LIGHTING AND RECEPTABLE OUTLET CIRCUITS
| Square footage of house | Calculation for watts used (square footage of house multipled by 3 for typical usage) | 3 watts/sq.ft. | --
| 2000 | 6000 |  | 6000
KITCHEN CIRCUITS
| Kitchen Circuits |  | 3,000 watts
| Electric Oven |  | 2,000 watts
| Electric stove top |  | 5,000 watts
| Microwave |  | 1,500 watts
| Garbage disposal under kitchen sink |  | 1,000 watts
| Automatic dish washer |  | 3,500 watts
| Garbage compactor |  | 1,000 watts
| Instantaneous hot water at sink |  | 1,500 watts
Laundry Circuit
| Laundry circuit |  | 1,500 watts
| Electric clothes dryer |  | 4,500 watts
HEATING AND AIR CONDITIONING CIRCUITS
| Central heating and air conditioning |  | 6,000 watts
| Window mounted air conditioning |  | 1,000 watts
| Whole-house or attic fan |  | 500 watts
| Central electric furnance |  | 8,000 watts
| Evaporative cooler |  | 500 watts
OTHER ELECTRICAL LOADS
| Electric water heater (storage type) |  | 4,000 watts
| Electric tankless water heater |  | 15,000 watts
| Swimming pool or spa |  | 3,500 watts
ELECTRIC VEHICLE CHARGER CIRCUIT
Level 2 electric vehicle charger wattage rating
|  |  | TOTAL WATTS USED | 6000

## Sheet2
INSTRUCTIONS: Using the "TOTAL WATTS USED" number from the previous page, check the appropriate line in column 1 and follow that line across to determine the minimum required size of the electrical service panel shown in column 3. In column 4, write in the size of your existing service panel (main breaker size). If your existing service panel (column 4) is smaller than the minimum require size of the existing service (column 3), then you will need to install a new upgraded electrical service panel to handle the added electrical load from the proposed Level 2 charger.
The table below is based on the CEC 220.83(A), 230.42 and Annex D
1 | 2 | 3 | 4
Check the appropriate line | Total Watts Used (from previous page) | Minimum Required Size of Existing 240-Volt Electrical Service Panel (Main Service Breaker Size - Amps) | Identify the Size of Your Existing Main Service Breaker (Amps)**
| Up to 48,000 | 100
| 48,801 to 63,000 | 125
| 63,001 to 78,000 | 150
| 78,001 to 108,000 | 200
| 108,001 to 123,000 | 225
**Note that the size of your existing service (column 4) MUST be equal to or larger than the Minimum Required Size (column 3) or a new larger electrical service panel will need to be installed in order to satisfy the electrical load demand of the EV charger
STATEMENT OF COMPLIANCE
By my signature, I attest that the information provied is true and accurate.
Job Address:
(Print job address)
Signature:
(Signature of applicant)
Date:
(Date)
In addition to this document, you will also need to provide a copy of the manufacturers installation literature and specifications for the Level 2 charger you are installing
Note: This is a voluntary compliance alternative and you may wish to hire a qualified individual or company to perform a thorough evaluation of your electrical service capacity in lieu of this alternative methodology. Use of this electrical load calculation estimate methodology is at the user’s risk and carries no implied guarantee of accuracy. Users of this methodology and these forms are advised to seek professional assistance in determining the electrical capacity of a service panel.